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Product Guide Specification


Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice, Fifth Edition.

This section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” after editing this section.

Section numbers are from MasterFormat 2010 Update.

SECTION 26 05 33.15
STAINLESS STEEL CONDUIT AND COUPLINGS

Specifier Notes:  Delete any information below in Parts 1, 2 or 3 which is not required or relevant for the project.

GENERAL

1.01	SUMMARY

A.	This section includes stainless steel rigid metal conduit and couplings for use in corrosion resistant environments.

B.	Related Sections:
	1.	Section 26 05 33.54	Industrial Grade Conduit Bodies
	2. 	Section 26 05 33.55	Industrial Grade Rigid Fittings

1.02    REFERENCES

National Fire Protection Association (NFPA):
		       1.  	     NFPA 70	          	        National Electrical Code (NEC)

American Society for Testing and Materials (ASTM):
ASTM A 312/SA 312: 	Standard Specification for Seamless and Welded Austenitic

Underwriters Laboratories, Inc. (UL):
		1.	UL 6A				Electrical Rigid Metal Conduit - Aluminum, Red Brass, and Stainless 
							Steel

            D.     Canadian Standard Association (CSA):
		1.	CSA C22.2 No.45.2	Electrical Rigid Metal Conduit - Aluminum, Red Brass, and Stainless 
							Steel
        2.	      CSA C22.1		        Canadian Electrical Code Part I
          
0. American National Standards Institute (ANSI):
0.  ANSI C80.1			American National Standard For Electrical Rigid Steel Conduit (ERSC)




1.03    SUBMITTALS

        A.       Comply with Section 01 33 00 – Submittal Procedures.

B.       Product Data:
0. Submit manufacturer’s descriptive literature and product specifications for each product.

1.04	QUALITY ASSURANCE

A.	Manufacturer Qualifications: Products shall be free of defects in material and workmanship. 

B.	Furnished products shall be listed and certified by third party agencies as suitable for the intended purpose.

1.05 WARRANTY

A. Product is warranted free of defects in material and workmanship.

B. Product is warranted to perform the intended function within design limits.

PRODUCTS

2.01   GENERAL

0. T&B® stainless steel conduit shall be UL listed to UL6A and UL classified to CSA C22.2 No.45.2.

0. T&B® stainless steel conduit shall comply with ASTM A-321/SA-312.

0. T&B® stainless steel conduit shall comply with ANSI C80.1.

2.02   MANUFACTURERS
          
A. Acceptable Manufacturers:	        
ABB Installation Products Inc. 
        860 Ridge Lake Boulevard
        Memphis, Tennessee 38120
        800-816-7809, 901-252-5000
        electrification.us.abb.com

                      Products: 	
3. T&B® Stainless Steel Conduit & Couplings

B.       Substitutions:  Not permitted.

2.03   MATERIALS / COMPONENTS 

0. T&B® stainless steel conduit shall be available in both 304 and 316 grade stainless steel.

T&B® stainless steel conduit couplings shall be available in 316 grade stainless steel.


2.04 DESIGN AND PERFORMANCE REQUIREMENTS

A. T&B® Stainless Steel Conduit
1.	T&B® stainless steel conduit shall be available in trade sizes from ½” to 4”.
2.	T&B® stainless steel conduit shall be available in the following series:
	a. 	COND1/2SS series (304 stainless steel)
	b.	COND1/2SST series (316 stainless steel)
3.	T&B® stainless steel conduit shall be provided with NPT threads on each end.
4.	T&B® stainless steel conduit shall be provided in standard lengths of 10 ft. with one stainless 
				steel coupling included.
5.	T&B® stainless steel conduit shall be polished to a bright, easily maintainable finish that allows for minimal cleaning and improves the surface's resistance to pitting & bacterial corrosion for clean-in-place and sterilize-in-place systems.
			6. 	T&B® stainless steel conduit shall be used with the following T&B® stainless steel fittings:
				a.	LU18SST series Form 8 conduit bodies per section 26 05 33.54
				b. 	H050GRSST series grounding hub per section 26 05 33.55
				c.	L050GR-SST series grounding and bonding locknut per section 26 05 33.55
				d.	HS101-SS and HS901-SS one-hole and two-hole pipe straps per section 26 05 33.55

B. T&B® Stainless Steel Coupling
1. T&B® stainless steel couplings shall be available in trade sizes from ½” to 4”.
2. T&B® stainless steel couplings shall be offered as the CPL1/2SST series.
3. T&B® stainless steel couplings shall be provided with NPS threads to thread onto T&B® stainless steel conduit.

EXECUTION

3.01	INSTALLATION

     Installation shall be in accordance with the NEC and CEC guidelines where applicable.
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